SECTION 271116 - COMMUNICATIONS CABINETS, RACKS, FRAMES, AND ENCLOSURES

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

GREAT LAKES DATA RACKS & CABINETS: G2EZ Series Data Rack / Cabinet

DEFINITIONS

BICSI: Building Industry Consulting Service International

EIA:  Electronic Industries Alliance.

TIA: Telecommunications Industry Association.

ANSI: American National Standard Institute.

LAN: Local area network.

RCDD: Registered Communications Distribution Designer.

REFERENCES

ANSI/TIA-569-D Telecommunications Pathways and Spaces, 2015

ANSI/TIA-568-D.0 Generic Telecommunications Cabling for Customer Premises, 2015

ANSI/TIA – 568-D.1 Commercial Building Telecommunications Cabling Standard, 2015.

ANSI/NECA/BICSI 568-2006 – Standard for Installing Commercial Building Telecommunications Cabling.

ANSI/TIA-942-A Telecommunications Infrastructure Standard for Data Centers, 2014.

ANSI/TIA – 606-B Administration Standard for Telecommunications Infrastructure, 2012.

ANSI/TIA – 607-C Generic Telecommunications Bonding and Grounding (Earthing) For Customer Premises, 2015.

ANSI/NFPA 70 – National Electric Code, 2008, 2014.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Shop Drawings: For communications equipment room fittings.

Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

Grounding: Indicate location of bonding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

INFORMATIONAL SUBMITTALS

Qualification Data: For [Installer] qualified layout technician, installation supervisor, and field inspector.

Seismic Qualification Certificates: For equipment frames from manufacturer.

Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Base certification on the maximum number of components capable of being mounted in each rack type. Identify components on which certification is based.

Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

QUALITY ASSURANCE

Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

Layout Responsibility: Preparation of Shop Drawings shall be under the direct supervision of [RCDD] [RCDD/NTS] [Commercial Installer, Level 2].

Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

Field Inspector: Currently registered by BICSI as [RCDD] [Commercial Installer, Level 2] to perform the on-site inspection.

PRODUCTS

- G2EZ SERIES DATA RACKS

Basis-of-Design Product: Subject to compliance with requirements, provide Great Lakes Data Racks & Cabinets (GLDRC); G2EZ SERIES Rack.

Color: [Black] textured powder coated steel

Seismic rated weight capacity, 1500lbs. NEBS GR-63-CORE Rated.

Max non seismic rated load, 5000lbs.

Constructed cold rolled steel.

Welded frame #12ga.  -

2 pair mounting rails #12ga.

Top panel #16ga.

Doors #16ga.

Side panels #18ga.

Front door, single perforated vented with keyed locking handle, all doors with field reversible hinges

Captive hinge type, with bonding wire and quick disconnect.

3-point latching rod system

Handle cutout, 25mm x 150mm

Rear doors, split perforated vented with keyed locking handle, all doors with field reversible hinges.

Captive hinge type, with bonding wire and quick disconnect.

2-point latching system

Handle cutout, 25mm x 150mm

Side panels, qty-4 per rack keyed quarter turn lock, solid.

Top Panel, Removable Solid Center, with Cable Access Knockouts

Optional Top Panels:

Brush Grommeted, Vented, 225 CFM Fan, 550 CFM Fan, 1100 CFM Fan

Mounting Rails: 3/8” Square Hole, with RMU Ascending Labels

Top Panel cable access with Optional brush grommet dust kits.

Power Strip Mounting, single mounting location in each rear corner, button mounting. Additional mounting on optional vertical cable bar.

Optional Internal Cable Management

Horizontal and Vertical Cable Bars

Plastic Cable separation fingers, 4” & 7” long options

Optional mounting to front or rear of EIA Rail

Cable rings, Metal with Cable Lacing slots

Optional mounting to front or rear of EIA Rail

Optional External Cable Management, G2EZ Series to accept:

Top Cable Troughs

Heavy Duty Cable troughs

Optional Air Flow Accessories

Brush Grommet Rail Kit, Mounts to EIA Rails, Air Flow separation

Size

The rack family of product must be Great Lakes product.

- model 45UG2EZ-2442, 19” EIA

Height: 45 RMU / 84”

Width: 24”

Rack Depth: 42”

Equipment Mounting: 3/8” Sq. Hole for Metric 6mm Cage nut hardware, included.

EXECUTION

INSTALLATION OF FLOOR MOUNTED EQUIPMENT RACKS

- Assemble racks according to manufacturer's instructions. Verify that equipment mounting rails are sized properly for rack-mount equipment before attaching the rack to the floor.

- Use GLDRC Part Number AK-101 for concrete slab floors.

All racks must be attached to the floor in four places using appropriate floor mounting anchors. When placed over a raised floor, threaded rods should pass through the raised floor tile and be secured in the structural floor below. Racks shall be grounded to the bonding busbar using appropriate hardware provided by the contractor. The bond will meet local code requirements and will be approved by the Authority Having Jurisdiction (AHJ).

Ladder rack may be attached to the top of the rack to deliver cables to the rack. The rack shall not be drilled to attach ladder rack. Use appropriate hardware from the ladder rack manufacturer.

The equipment load will be evenly distributed and uniform on the rack. Place large and heavy equipment towards the bottom of the rack. Secure all equipment to the rack with equipment mounting screws. In seismic areas, secure equipment to shelves with additional bracing.

Accessory Equipment Mounting Rails:  Equipment must be attached to the equipment mounting rails and must not exceed the accessory equipment mounting rails load capacity.  Verify that the rack has sufficient load capacity for the accessory equipment mounting rails and equipment.

Shelves:  Equipment placed on the shelf must fit completely within the shelf surface and must not exceed the shelf load capacity.  Verify that the rack has sufficient load capacity for the shelf and equipment.

Cable Runway Mounting Bracket:  Install according to manufacturer's instructions.

END OF SECTION 271100