SECTION 271116 - COMMUNICATIONS CABINETS, RACKS, FRAMES, AND ENCLOSURES

PART 1 - GENERAL

1.1	RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2	SUMMARY

Section Includes:

1.	4 POST RACK – 29” FIXED DEPTH, #12-24 THREADED MOUNTING

1.3	DEFINITIONS

A.	BICSI: Building Industry Consulting Service International

B.	EIA:  Electronic Industries Alliance.

C.	TIA: Telecommunications Industry Association.

D.	ANSI: American National Standard Institute.

E.	LAN: Local area network.

F.	RCDD: Registered Communications Distribution Designer.

1.4	REFERENCES

A.	ANSI/TIA-569-D Telecommunications Pathways and Spaces, 2015

B.	ANSI/TIA-568-D.0 Generic Telecommunications Cabling for Customer Premises, 2015

C.	ANSI/TIA – 568-D.1 Commercial Building Telecommunications Cabling Standard, 2015.

D.	ANSI/NECA/BICSI 568-2006 – Standard for Installing Commercial Building Telecommunications Cabling.

E.	ANSI/TIA-942-A Telecommunications Infrastructure Standard for Data Centers, 2014.

F.	ANSI/TIA – 606-B Administration Standard for Telecommunications Infrastructure, 2012.

G.	ANSI/TIA – 607-C Generic Telecommunications Bonding and Grounding (Earthing) For Customer Premises, 2015.

H.	ANSI/NFPA 70 – National Electric Code, 2008, 2014.

1.5	ACTION SUBMITTALS

A.	Product Data: For each type of product.

1.	Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

2.	Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

B.	Shop Drawings: For communications equipment room fittings.

1.	Include plans, elevations, sections, details, and attachments to other work.

2.	Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3.	Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

4.	Grounding: Indicate location of bonding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

1.6	INFORMATIONAL SUBMITTALS

A.	Qualification Data: For [Installer] qualified layout technician, installation supervisor, and field inspector.

B.	Seismic Qualification Certificates: For equipment frames from manufacturer.

C.	Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

1.	Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Base certification on the maximum number of components capable of being mounted in each rack type. Identify components on which certification is based.

2.	Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

1.7	QUALITY ASSURANCE

A.	Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

B.	Layout Responsibility: Preparation of Shop Drawings shall be under the direct supervision of [RCDD] [RCDD/NTS] [Commercial Installer, Level 2].

1.	Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall always be present when Work of this Section is performed at Project site.

2.	Field Inspector: Currently registered by BICSI as [RCDD] [Commercial Installer, Level 2] to perform the on-site inspection.

PART 2 - PRODUCTS

2.1	RACKS

A.	Basis-of-Design Product: Subject to compliance with requirements, provide Great Lakes Data Racks & Cabinets (GLDRC); Standard 4P FOUR POST 24” FIXED DEPTH RACK.

1.	Finish: Textured Black Powder Coat

2.	UL 2416 Listed: 1500lbs Capacity.

3.	Material:

a.	Vertical Upright, Top & Depth Angles: #12 ga. Cold Rolled Steel

b.	Base Angles: #7 ga. Cold Rolled Steel

4.	Vertical Channel to be 3” Deep with networking side facing holes and have #12-24 threaded holes on front and rear mounting surfaces.

5.	Assembly Hardware of ½”-13 Threaded Hardware.

6.	Main Bonding 2 Hole Lug provided.

7.	4 POST RACK must include:

a.	(4) Vertical Upright Channel, 3” Deep

b.	(2) Base Angles

c.	(2) Top Angles

d.	(2) Base Depth Angles

e.	(2) Top Depth Angles

f.	(24) ½”-13 x 1” Lg Hex Head Bolts & (24) ½” Lock washers & (24) Hex Nuts

g.	(50) #12-24 x ½” Long Phillips Head Screws

h.	(1) Double Hole Bonding Lug

8.	Rack EIA 310-E Width of 19” EIA

9.	Rack Mounting Units (RMU) Numerically Labeled in Ascending order, bottom to top

10.	Country of Origin Made in the USA

11.	RMU: 45

12.	Channel Depth: 29”

13.	Overall Depth: 41” with toe out orientation

14.	Overall Width: 20”

B.	MODEL NUMBER AND SIZE

1.	4P-45U29-B-1224

C.	OPTIONAL ACCESSORIES

1.	Vertical Cable Managers, Power Strip Bracket.

a. 	VCMP-55FO; 5” X 5” Front Only, includes snap on cover

b. 	VCMP-55FR; 5” X 5” Front and Rear includes snap on covers

c. 	VCMP-88FO; 8” X 8” Front Only, includes spools and hinged cover

d.	VCMP-88FR; 8” X 8” Front and Rear includes spools and hinged covers

e.	1984LR; Ladder Rack support bracket, supports 12” and 18” wide cable tray

f.	PSBGLRR; Power Strip Bracket kit, single vertical basic power strip

PART 3 - EXECUTION

3.1	INSTALLATION OF FLOOR MOUNTED EQUIPMENT RACKS

Assemble racks according to manufacturer's instructions. Verify that equipment mounting rails are sized properly for rack-mount equipment before attaching the rack to the floor.

Use GLDRC Part Number AK-101 for concrete slab floors.

All racks must be attached to the floor in four places using appropriate floor mounting anchors. When placed over a raised floor, threaded rods should pass through the raised floor tile and be secured in the structural floor below. Racks shall be grounded to the bonding busbar using appropriate hardware provided by the contractor. The bond will meet local code requirements and will be approved by the Authority Having Jurisdiction (AHJ).

Ladder rack may be attached to the top of the rack to deliver cables to the rack. The rack shall not be drilled to attach ladder rack. Use appropriate hardware from the ladder rack manufacturer.

The equipment load will be evenly distributed and uniform on the rack. Place large and heavy equipment towards the bottom of the rack. Secure all equipment to the rack with equipment mounting screws. In seismic areas, secure equipment to shelves with additional bracing.

A.	Accessory Equipment Mounting Rails:  Equipment must be attached to the equipment mounting rails and must not exceed the accessory equipment mounting rails load capacity.  Verify that the rack has sufficient load capacity for the accessory equipment mounting rails and equipment.

B.	Shelves:  Equipment placed on the shelf must fit completely within the shelf surface and must not exceed the shelf load capacity.  Verify that the rack has sufficient load capacity for the shelf and equipment.

C.	Cable Runway Mounting Bracket:  Install according to manufacturer's instructions.

END OF SECTION 271100