SECTION 271116 - COMMUNICATIONS CABINETS, RACKS, FRAMES, AND ENCLOSURES

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

GREAT LAKES DATA RACKS & CABINETS : L Series Data Rack / Cabinet

DEFINITIONS

BICSI: Building Industry Consulting Service International

EIA:  Electronic Industries Alliance.

TIA: Telecommunications Industry Association.

ANSI: American National Standard Institute.

LAN: Local area network.

RCDD: Registered Communications Distribution Designer.

REFERENCES

ANSI/TIA-569-D Telecommunications Pathways and Spaces, 2015

ANSI/TIA-568-D.0 Generic Telecommunications Cabling for Customer Premises, 2015

ANSI/TIA – 568-D.1 Commercial Building Telecommunications Cabling Standard, 2015.

ANSI/NECA/BICSI 568-2006 – Standard for Installing Commercial Building Telecommunications Cabling.

ANSI/TIA-942-A Telecommunications Infrastructure Standard for Data Centers, 2014.

ANSI/TIA – 606-B Administration Standard for Telecommunications Infrastructure, 2012.

ANSI/TIA – 607-C Generic Telecommunications Bonding and Grounding (Earthing) For Customer Premises, 2015.

ANSI/NFPA 70 – National Electric Code, 2008, 2014.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Shop Drawings: For communications equipment room fittings.

Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

Grounding: Indicate location of bonding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

INFORMATIONAL SUBMITTALS

Qualification Data: For [Installer] qualified layout technician, installation supervisor, and field inspector.

Seismic Qualification Certificates: For equipment frames from manufacturer.

Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Base certification on the maximum number of components capable of being mounted in each rack type. Identify components on which certification is based.

Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

QUALITY ASSURANCE

Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

Layout Responsibility: Preparation of Shop Drawings shall be under the direct supervision of [RCDD] [RCDD/NTS] [Commercial Installer, Level 2].

Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

Field Inspector: Currently registered by BICSI as [RCDD] [Commercial Installer, Level 2] to perform the on-site inspection.

PRODUCTS

L SERIES DATA RACKS

Basis-of-Design Product: Subject to compliance with requirements, provide Great Lakes Data Racks & Cabinets (GLDRC) ; L SERIES Rack.

Color: [Black] textured powder coated steel

UL 2416 Listed: 3080lbs (1400kg)Capacity, static

Constructed cold rolled steel

Welded frame #11ga. & #16ga.

2 pair mounting rails #13ga.

Top panel #18ga.

Doors and side panel #22ga.

Front door, single hexagon perforated vented with keyed locking handle

Concealed lift off hinge type, with bonding wire and quick disconnect

Handle cutout, 25mm x 150mm

Rear doors, double hexagon perforated vented with keyed locking handle

Concealed lift off hinge type, with bonding wire and quick disconnect

Handle cutout, 25mm x 150mm

Side panels, qty-4 per rack each with keyed lock, solid.

Top Panel, provisions for optional fan tray and cable access cut out, Solid

Casters, installed, qty-2, Rigid, qty-2 Swivel

Leveling Glides, qty-4, installed.

Cable Management Bar, qty-1 installed, with powerstrip mounting provisions

Optional Cable Bar with metal rings, Field Depth adjustable

Size

The rack family of product must be Great Lakes product

- model GL790L-2442MSS, 19” EIA

Height: 42 RMU, 78.5”

Width: 24” / 600mm

Rack Depth: 42” / 1000mm

Equipment Mounting: [3/8” Sq. Hole for Metric 6mm Cage nut hardware, included]

EXECUTION

INSTALLATION OF FLOOR MOUNTED EQUIPMENT RACKS

- Assemble racks according to manufacturer's instructions. Verify that equipment mounting rails are sized properly for rack-mount equipment.

Racks shall be grounded to the bonding busbar using appropriate hardware provided by the contractor. The bond will meet local code requirements and will be approved by the Authority Having Jurisdiction (AHJ).

The equipment load will be evenly distributed and uniform on the rack. Place large and heavy equipment towards the bottom of the rack. Secure all equipment to the rack with equipment mounting screws. In seismic areas, secure equipment to shelves with additional bracing.

Accessory Equipment Mounting Rails:  Equipment must be attached to the equipment mounting rails and must not exceed the accessory equipment mounting rails load capacity.  Verify that the rack has sufficient load capacity for the accessory equipment mounting rails and equipment.

Shelves:  Equipment placed on the shelf must fit completely within the shelf surface and must not exceed the shelf load capacity.  Verify that the rack has sufficient load capacity for the shelf and equipment.

END OF SECTION 271100