SECTION 271116 - COMMUNICATIONS CABINETS, RACKS, FRAMES, AND ENCLOSURES

PART 1 - GENERAL

1.1	RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2	SUMMARY

Section Includes:

1.	ES Series Cabinet

1.3	DEFINITIONS

A.	BICSI: Building Industry Consulting Service International

B.	EIA:  Electronic Industries Alliance.

C.	TIA: Telecommunications Industry Association.

D.	ANSI: American National Standard Institute.

E.	LAN: Local area network.

F.	RCDD: Registered Communications Distribution Designer.

1.4	REFERENCES

A.	ANSI/TIA-569-D Telecommunications Pathways and Spaces, 2015

B.	ANSI/TIA-568-D.0 Generic Telecommunications Cabling for Customer Premises, 2015

C.	ANSI/TIA – 568-D.1 Commercial Building Telecommunications Cabling Standard, 2015.

D.	ANSI/NECA/BICSI 568-2006 – Standard for Installing Commercial Building Telecommunications Cabling.

E.	ANSI/TIA-942-A Telecommunications Infrastructure Standard for Data Centers, 2014.

F.	ANSI/TIA – 606-B Administration Standard for Telecommunications Infrastructure, 2012.

G.	ANSI/TIA – 607-C Generic Telecommunications Bonding and Grounding (Earthing) For Customer Premises, 2015.

H.	ANSI/NFPA 70 – National Electric Code, 2008, 2014.

1.5	ACTION SUBMITTALS

A.	Product Data: For each type of product.

1.	Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

2.	Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

B.	Shop Drawings: For communications equipment room fittings.

1.	Include plans, elevations, sections, details, and attachments to other work.

2.	Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3.	Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

4.	Grounding: Indicate location of bonding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

1.6	INFORMATIONAL SUBMITTALS

A.	Qualification Data: For [Installer] qualified layout technician, installation supervisor, and field inspector.

B.	Seismic Qualification Certificates: For equipment frames from manufacturer.

C.	Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

1.	Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Base certification on the maximum number of components capable of being mounted in each rack type. Identify components on which certification is based.

2.	Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

1.7	QUALITY ASSURANCE

A.	Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

B.	Layout Responsibility: Preparation of Shop Drawings shall be under the direct supervision of [RCDD] [RCDD/NTS] [Commercial Installer, Level 2].

1.	Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

2.	Field Inspector: Currently registered by BICSI as [RCDD] [Commercial Installer, Level 2] to perform the on-site inspection.

PART 2 - PRODUCTS

2.1	ES SERIES CABINET

Basis-of-Design Product: Subject to compliance with requirements, provide Great Lakes Data Racks & Cabinets (GLDRC); ES SERIES Rack.

Color: Black textured powder coated steel

UL 2416 Listed: 3300 lb Capacity, static

Constructed cold rolled steel

Welded frame #12ga. & #14ga.

2 pair mounting rails #12ga.

Top panel #16ga.

Doors and side panel #16ga.

Front door: mesh round contour with keyed locking lever handle;all doors with field reversible hinges

Lift off hinge type, with bonding wire and quick disconnect

Handle cutout, 25mm x 150mm

Rear door: mesh round contour with keyed locking lever handle; all doors with field reversible hinges

Lift off hinge type, with bonding wire and quick disconnect

Handle cutout, 25mm x 150mm

Side panels: Two solid sides with keyed lock

Top of Cabinet Frame: Cable access: rear center laser etched access, removable for exhaust chimney or cable access

Top Panel: Removable; Solid Top Panel

Bottom Panel: Removable; Optional: Solid center panel and solid rear panel; Brush grommet center panel and brush grommet rear panel

Mounting Rails: Two pair of 3/8” (M6) Square Hole with RMU ascending labels; rails feature Flexible Mounting Profile (FMP) for zero-U accessory mounting; support 19” EIA equipment

Leveling Glides: qty-4, installed

Casters: Optional: plate casters, swivel

Power Strip Mounting, 2 Pair of Adjustable Height Brackets included, for button mounting; brackets include three mounting positions for PDUs and Great Lakes vertical cable troughs

Optional Internal Cable Management

Horizontal and Vertical Cable Bars

Vertical Cable Trough, with Hinged cover & Zero U Mtg. options

Cable Trough, Front to rear

Plastic Cable separation fingers, 4” & 7” long options

Optional mounting to front or rear of EIA Rail

Cable rings, Metal with Cable Lacing slots

Optional mounting to front or rear of EIA Rail

Optional External Cable Management:

Top Cable Troughs

Heavy Duty Cable troughs

Ladder Rack support brackets

Waterfall Ladder Rack support brackets

External Cable “SIDE CAR”, 6” or 12” wide, with locking hinged doors

- w/ (2) depth adjustable vertical cable troughs, height & depth specific.

Optional Air Flow Accessories

Brush Grommet Rail Kit, Mounts to EIA Rails, Air Flow separation

Brush Grommet, Frame Pass through kits,

Exhaust Chimneys, Passive or Active (fan), height adjustable, depth specific. Up to 2200 cfm

Air Manager, Passive or Active (fan), up to 940 cfm.

Rack Mounting Units (RMU) numerically labeled in ascending order, bottom to top

Country of Origin, Made in the USA

RMU Height: 44 RMU, 84”

Width: 24

Depth: 42

B.	MODEL NUMBER

1)	GL840ES-2442-B-MS

PART 3 - EXECUTION

  - INSTALLATION OF FLOOR MOUNTED EQUIPMENT RACKS

- Assemble racks according to manufacturer's instructions. Verify that equipment mounting rails are sized properly for rack-mount equipment.

- Racks shall be grounded to the bonding busbar using appropriate hardware provided by the contractor. The bond will meet local code requirements and will be approved by the Authority Having Jurisdiction (AHJ).

- Ladder rack may be attached to the top of the rack to deliver cables to the rack. The rack shall not be drilled to attach ladder rack. Use appropriate hardware from the ladder rack manufacturer.

- The equipment load will be evenly distributed and uniform on the rack. Place large and heavy equipment towards the bottom of the rack. Secure all equipment to the rack with equipment mounting screws. In seismic areas, secure equipment to shelves with additional bracing.

- Accessory Equipment Mounting Rails:  Equipment must be attached to the equipment mounting rails and must not exceed the accessory equipment mounting rails load capacity.  Verify that the rack has sufficient load capacity for the accessory equipment mounting rails and equipment.

- Shelves:  Equipment placed on the shelf must fit completely within the shelf surface and must not exceed the shelf load capacity.  Verify that the rack has sufficient load capacity for the shelf and equipment.

END OF SECTION 271100

Additional ES Cabinets Available
Note that family size is listed below; these are not actual part numbers. To configure an ES cabinet and generate a part number, visit GreatCabinets.com

- GL480ES-2442 24 RMU, 48"H, 24 RMU; 19" EIA assembly, 24" W, 42” D

- GL790ES-2442 42 RMU, 79"H, 42 RMU; 19" EIA assembly, 24" W, 42” D

- GL790ES-2448 42 RMU, 79"H, 42 RMU; 19" EIA assembly, 24" W, 48” D

- GL790ES-3042 42 RMU, 79"H, 42 RMU; 19" EIA assembly, 30" W, 42” D

- GL790ES-3048 42 RMU, 79"H, 42 RMU; 19" EIA assembly, 30" W, 48” D

- GL840ES-2442 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 24" W, 42” D

- GL840ES-2448 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 24" W, 48” D

- GL840ES-3042 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 30" W, 42” D

- GL840ES-3048 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 30" W, 48” D

- GL840ES-3240 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 32" W, 40” D

- GL840ES-3242 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 32" W, 42” D

- GL840ES-3248 44 RMU, 84"H, 44 RMU; 19" EIA assembly, 32" W, 48” D

- GL910ES-2442 48 RMU, 91"H, 48 RMU; 19" EIA assembly, 24" W, 42” D

- GL910ES-2448 48 RMU, 91"H, 48 RMU; 19" EIA assembly, 24" W, 48” D

- GL910ES-3042 48 RMU, 91"H, 48 RMU; 19" EIA assembly, 30" W, 42” D

- GL910ES-3048 48 RMU, 91"H, 48 RMU; 19" EIA assembly, 30" W, 48” D